## Sheet1
Slave ID (HEX) | Function Code (HEX) | Sender Device | Responding Device | Request Message (HEX) | Response Message (HEX) | Note
1 | 3 | Control Panel 1 |  | 0 0 0 12
2 | 3 | Control Panel 1 |  | 0 0 0 12
2 | 3 | Control Panel 1 | Evap Unit | 00 18 00 20 | 40 00 02 00 02 00 0E 00 2E 03 YY 0D ZZ 00 00 00 00 00 F8 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 1D 2E B1 00 00 00 00 00 00 00 00 30 XX 00 00 00 00 00 00 WW QQ UU RR 00 TT XX = Running fan speed YY = Unknown (Observed BB, D1, D2, D3, D4) (D1-D4 slow increment over time) ZZ = Unknown (Observed 1A, 37, 38) WW = 0x10 When off, 0x10 + Fan Speed when running. Example: 15 = Cooler/FAN 5, 16 = Cooler/FAN 6 QQ = 1 when off, 4 when cooler starting or fan running, then 14, then 16 when running (possible pump / water state?) 5 when Fan running. UU= 0 Possible Water Salinity Sensor – Only increases from 0 when cooler is run, maintains and slowly drops. Immediate drop to 0 after triggering manual drain (tested once). RR = 0 When Off/Fan Mode, various values when Cooler running. TT = 0 When Off/Fan Mode, slowly increments when cooler running. Offline: 40 00 02 00 02 00 0E 00 2E 03 BB 0D 1A 00 00 00 00 00 F8 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 1D 2E B1 00 00 00 00 00 00 00 00 30 00 00 00 00 00 00 00 10 01 00 00 00 00 Variable seems to stay when idle, Bytes 11 and 13 observed changes. | Status request from CP1 to AC Unit
2 | 3 | Control Panel 1 | Evap Unit | 00 1D 00 01 | 02 0D XX Observed: 02 0D 1A 02 0D 37 02 0D 20 02 0D 23 02 0D 3B 02 0E CB – Cooler Speed 6 02 0E CE
2 | 3 | Control Panel 1 | Evap Unit | 00 35 00 01 | 2 10 XX 2 10 0 2 10 1 2 16 16 2 13 16 2 15 16
2 | 3 | Control Panel 1 | Evap Unit | 00 00 00 12 | 24 10 34 20 10 5A 45 00 51 00 9B 00 00 00 SS SS SS 00 02 00 03 10 6D 00 00 00 00 00 00 00 00 00 42 01 09 81 58 24 10 34 20 10 MM MM MM MM 00 MM 00 00 00 SS SS SS 00 02 00 WW WW WW 00 00 00 00 00 00 00 00 00 42 01 09 81 58 | TYPE: EVAPORATIVE COOLER MODEL: BREEZAIR EZQ 155 – MM (2-Byte Reversal) SERIAL NO - SS Last Running State:– Not included in message, fan or cooler mode does not change response. S/W VERSION: 20R0813 – WW (0x031062 = 200813 = 20R0813)"
2 | 10 | Control Panel 1 | Evap Unit | 00 31 00 01 02 30 XX Observed with Fan On: 00 31 00 01 02 30 20 00 31 00 01 02 30 30 With cooler on (pump on, drain closed) 00 31 00 01 02 30 52 (speed 5) 00 31 00 01 02 30 62 (speed 6) Off: 00 31 00 01 02 30 00 | 00 31 00 01 | XX = Fan Speed, 10 = Speed 1, 20 = Speed 2 ect, +2 for Cooler Mode. +1 when drain open. Appears to be command used by panel to trigger aircon unit.
8C | 3 | Control Panel 1 | Heater or Zone Control | 0 6F 0 B | 16 2 B2 1 66 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 4 0 10 16 2 B2 1 66 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 4 0 11 16 2 B2 1 66 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 4 0 12 16 2 B2 1 66 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 4 0 13 16 2 B2 1 66 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 4 0 14 16 2 B2 1 66 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 4 0 15 16 2 B2 1 66 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 4 0 16 16 2 B2 1 66 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 4 0 17 16 2 B2 1 66 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 4 0 18 16 2 B2 1 66 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 4 0 19 16 2 B2 1 66 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 4 0 1A 16 2 B2 1 66 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 4 0 1B 16 2 B2 1 66 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 4 0 F
8D | 3 | Control Panel 1 | Heater or Zone Control | 00 64 00 3B | 8D 03 64 08 A0 00 00 00 00 00 8D 00 00 00 00 00 00 00 00 00 00 3A 30 00 00 02 B2 01 66 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 04 00 21 1E 40 51 54 00 00 00 00 00 SS SS SS 04 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 81 09 00 00 04 04 | Query and response occurred when going to About Heater information section on CP1. Returned info: Type: GAS DUCTED HEATER Model: BRAEMAR HEATING TQ420N SERIAL: SSSSSS S/W Version: V1.09 DATA TABLE VERSION: D0.00
8D | 3 | Control Panel 1 | Heater or Zone Control | 00 94 00 07 | 0E 00 00 04 04 04 04 04 04 00 04 00 00 69 A8 Observed when heater running history requested: C 2 B2 1 66 0 0 0 0 0 0 0 0 On Fault log request: 3C 4 4 4 4 4 4 0 4 0 0 69 A8 71 85 19 32 0 0 81 4 2C C1 29 73 B 23 9D 26 6D CC BA 60 B8 3A 9B EC 28 B4 45 90 5E F3 B 53 6F E4 C2 E3 5F E4 F1 D1 3 70 F5 53 F7 3 3E 5B | Diagnostic info request to heater.
8D | 10 | Control Panel 1 | Heater or Zone Control | 00 63 00 02 04 10 XX 08 A0 | 00 63 00 02 | XX = 00 When Idle, C1 When Fan mode on recycle speed 1, also seen 80 after turned off.
8D | 10 | Control Panel 1 | Heater or Zone Control | 00 6E 00 01 02 00 00 | 00 6E 00 01
8D | 10 | Control Panel 1 | Heater or Zone Control | 0 9B 0 2 4 XX YY Variable Entry: XX YY – Seems to be linked to number of seconds – or internal flame sensor temp? Observed responses: 0 9B 0 2 4 0 24 2C F2 0 9B 0 2 4 0 45 2C F2 0 9B 0 2 4 0 67 2C F2 0 9B 0 2 4 0 88 2C F2 0 9B 0 2 4 0 AA 2C F2 0 9B 0 2 4 0 CA 2C F2 0 9B 0 2 4 0 EC 2C F2 0 9B 0 2 4 1 2F 2C F2 | 0 9B 0 2 | Information update from CP1 - unsure of what.
97 | 3 | Control Panel 1 | Control Panel 2 | 00 CD 00 02 | 04 00 00 00 00
97 | 3 | Control Panel 1 | Control Panel 2 | 00 E5 00 01 | 02 XX 00 02 19 11 (CRC: 3B C5) | XX = Temp in Zone 2 (untested but matched at 0x14 = 20C) Fan Speed in code: 00 CD 00 02 04 00 XX 00 A8 Where XX = Fan speed.
97 | 3 | Control Panel 2 |  | 22 00 00 00 00 4F 44 4E 57 54 53 49 41 53 52 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 53 00 00 03 E9 |  | Startup Code
97 | 10 | Control Panel 1 | Control Panel 2 | 00 C7 00 05 0A XX XX YY YY 30 52 ZZ ZZ 80 00 | 00 C7 00 05 Observed Queries: 00 C7 00 05 0A EF 2C 2D 09 30 52 00 00 80 00 00 C7 00 05 0A EF 19 2D 09 30 52 00 00 80 00 00 C7 00 05 0A EF 20 2D 09 30 52 00 00 80 00 00 C7 00 05 0A EF 26 2D 09 30 52 00 00 80 00 00 C7 00 05 0A EF 2C 2D 09 30 52 00 00 80 00 00 C7 00 05 0A E0 BF 2C FC 30 52 64 00 80 00 00 C7 00 05 0A FF D2 2C F2 30 52 64 00 80 00 00 C7 00 05 0A FF D8 2C F2 30 52 64 00 80 00 00 C7 00 05 0A FF DF 2C F2 30 52 64 00 80 00 | Control panel 2 uptime. 00C7 = First register for time update. 0005 = Registers to Write 0A = 10 Bytes. XXXX = Seconds YYYY = Seconds Multiplier ZZZZ = Unknown Usage 6400 or 0000 Observed. Time is calculated by YYYY Dec Value x 65535 + XXXX Dec Value Time start 1/1/2000 02:55:00 Approx. – odd start time.
97 | 10 | Control Panel 1 | Control Panel 2 | 00 CD 00 02 04 00 XX 00 A8 Observed Queries: 00 CD 00 02 04 00 06 00 A8 | 00 CD 00 02 | XX = Zone 1 Max Fan Speed
97 | 10 | Control Panel 1 | Control Panel 2 | 00 EF 00 02 04 02 X7 00 00 00 EF 00 02 04 02 C6 00 15 (CRC: 7E 67) | 00 EF 00 02 | X7 = Increments when IOT command received, matches command number sent by IOT Module in EB 10 1A
A5 | 3 | Control Panel 1 |  | 1 2C 0 8
D3 | 3 | Unknown - Not CP1 or IOT |  |  |  | Occurs after CP1 startup occurred
D4 | 3 | Control Panel 1 | Heater or Zone Control | 0 FB 0 6 | C 3 1 FF FF FF FF FF FF FF FF 0 0
D4 | 10 | Control Panel 1 | Heater or Zone Control | 00 FA 00 01 02 00 03 50 9E | 00 FA 00 01 | may need to be re-checked.
D5 | 3 | Unknown - Not CP1 or IOT |  | 0 FA 0 7 |  | Response after CP1 Startup Occurred
D6 | 3 | Unknown - Not CP1 or IOT |  | 0 FA 0 7 |  | Response after CP1 Startup Occurred
D6 | 10 | Control Panel 1 | Heater or Zone Control | 00 FA 00 01 02 00 XX | 00 FA 00 01 | XX = 1 or 0, observed 0 offline, 1 with control panel alone.
EB | 3 | Control Panel 1 | IOT | 02 58 00 12 (CRC: 53 66) | 24 00 XX 52 4D 32 48 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 04 00 24 00 00 52 4D 32 48 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 04 00 (CRC: 83 35) | EB not observed while IOT module is connected with account not logged in. XX Values: 21 = WiFi Disconnected, 00 = Connected
EB | 3 | Control Panel 1 | IOT | 0B 0C 00 0D (CRC 50 E2) | 1A x1 x2 x3 x4 x5 x6 x7 x8 00 x10 00 x12 00 x14 00 00 00 14 00 00 00 00 00 00 00 00 1A 02 9F 21 11 42 43 04 A2 00 24 00 24 00 01 00 00 00 12 00 00 00 00 00 00 00 00 (CRC: 86 E3) | X1, X2 = 2 Byte pair Increases +1 on each command recieved X3 = -db value of wireless signal strength. (Shows -68db or lower if disconnected) X4 – 10 = On, 11 = Off System On/Off X5 – Cooler Mode Enable/Disable 0x42 = Off, 0x02 = Enabled (Fanspeed Mode), 0x22 = Enabled (Temp Mode) 0x43 observed +/- 1 value unknown link X6 – Evap Unit Fan Settings (Code = 41 + Fanspeed x 2) +2 for fan increase, -2 for fan speed decrease 42 While recycle fan mode enabled (-1 When Recycle Mode Enabled) In Temp Mode x5 x6 are 2 byte pair 0x22 0x80 for 20C : +/- 20 for temp changes per degree. +80 increase occurs but unsure why (occured while running ext fan) X7 = 04,05,06 - Unsure if 2 byte pair with x8 X8 – Heater Fan Settings Unknown larger increment occurs. Swapping to cooler mode from ext fan -20 Swapping to ext fan to cooler mode +20 Value doesnt change on ext fan mode when changing speeds. 0x02 - Cooler Mode 0x22 - External Fan Mode 0x23 - Recycle fan speed 1 0x25 - Recycle fan speed 2
EB | 3 |  |  |  |  | Heater Temp: x7 and x8 combined in byte pair. +0x40 = +1 Degree, 0 Degrees = 02 C3 (Start index) Fan External Mode - 0xA2 Cooler Mode - 0x82 Swapping to cooler mode from ext fan -20 Swapping to ext fan to cooler mode +20 Value doesnt change on ext fan mode when changing speeds. X10, X12 - Cooler Temperature Target = Temp x2 eg 0x30 = 24C X14 - Zone Control +/- 1 = Zone 1 (Upstairs), +/- 2 Zone 2 (Downstairs)"""" X15 = 0x00 (Guessing zone 4) X16 = 0x00 (Guessing zone 3) X17 = Zone 2 Temp (heater) X18 = Zone 1 Temp (Heater)
EB | 3 | Control Panel 1 | IOT | 03 E4 00 05 (CRC: D3 70) | 0A VV VV VV VV ZZ XX YY WW UU QQ | Sent when viewing module info. Version: VV and IOT Unit MAC address: XX-ZZ-WW-YY-QQ-UU
EB | 10 | Control Panel 1 | IOT | 5 D8 0 23 46 0 1 0 49 50 55 54 53 49 41 53 52 0 0 0 0 0 0 0 0 0 0 0 0 4F 44 4F 44 4E 57 54 53 49 41 53 52 0 0 0 0 0 0 0 0 0 0 4F 5A 4F 5A 45 4E 33 20 0 0 0 0 0 0 0 0 0 0 0 0 0 0 4F 5A | 5 D8 0 23 | No Changes Observed
EB | 10 | Control Panel 1 | IOT | 5 FB 0 21 42 4F 5A 45 4E 34 20 0 0 0 0 0 0 0 0 0 0 0 0 0 0 4F 5A 4F 5A 45 4E 35 20 0 0 0 0 0 0 0 0 0 0 0 0 0 0 4F 5A 4F 5A 45 4E 36 20 0 0 0 0 0 0 0 0 0 0 0 0 0 0 4F 5A | 5 FB 0 21 | No Changes Observed
EB | 10 | Control Panel 1 | IOT | 6 1C 0 2C 58 4F 5A 45 4E 37 20 0 0 0 0 0 0 0 0 0 0 0 0 0 0 4F 5A 4F 5A 45 4E 38 20 0 0 0 0 0 0 0 0 0 0 0 0 0 0 4F 5A 4F 5A 45 4E 39 20 0 0 0 0 0 0 0 0 0 0 0 0 0 0 4F 5A 4F 5A 45 4E 31 20 0 30 0 0 0 0 0 0 0 0 0 0 0 0 4F 43 | 6 1C 0 2C | No Changes Observed
EB | 10 | Control Panel 1 | IOT | 6 48 0 4 8 0 40 0 0 0 0 0 0 | 6 48 0 4 | No Changes Observed
EB | 10 | Control Panel 1 | IOT | 06 4C 00 38 70 00 05 17 44 45 5A 51 20 31 35 35 00 00 00 00 00 00 00 00 02 00 03 10 6D 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 | 6 4C 0 38 | No Changes Observed
EB | 10 | Control Panel 1 | IOT | 6 84 0 2A 54 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 | 6 84 0 2A | No Changes Observed
EB | 10 | Control Panel 1 | IOT | 6 AE 0 2A 54 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 | 6 AE 0 2A | No Changes Observed
EB | 10 | Control Panel 1 | IOT | 6 D8 0 19 32 4 XX 0 0 12 1C 0 A0 54 51 34 33 30 4E 0 0 0 0 0 0 0 0 0 0 0 3 1E 8D 0 8D 81 9 69 A8 0 0 0 YY 3 8A 0 1 12 1C 0 F4 12 1C 0 12 | 6 D8 0 19 | Observed value changes: XX = 50, YY = 25 XX = 34, YY = 23
EB | 10 | Control Panel 1 | IOT | 08 E5 00 01 02 X1 X2 08 E5 00 01 02 00 00 (Observed While System Off) 08 E5 00 01 02 00 01 (Observed While System ON) | 08 E5 00 01 (CRC: 04 94) | X1,X2 = Changes on On/Off Value increments +10 when changed by Control Panel. 1 For On 0 For Off Appears to be command from CP1 to Turn On/Off IOT State and indicate panel settings change.
EB | 10 | Control Panel 1 | IOT | 08 E6 00 32 64 00 00 00 CF 00 A9 01 40 00 3C 00 00 00 00 00 02 00 02 00 0E 00 2E 03 D0 0D 37 00 00 00 00 00 00 00 00 0C 00 00 14 00 12 02 B2 01 66 00 00 00 00 00 00 00 00 00 00 04 04 04 04 00 04 00 00 00 00 00 50 00 50 00 00 00 00 00 00 00 00 00 00 00 00 9D 14 15 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 08 E6 00 32 64 00 00 00 D0 00 A9 01 40 00 3C 00 00 00 00 00 02 00 02 00 0E 00 2E 03 D0 0D 37 00 00 00 00 00 00 00 00 0C 00 00 14 00 12 02 B2 01 66 00 00 00 00 00 00 00 00 00 00 04 04 04 04 00 04 00 00 00 00 00 50 00 50 00 00 00 00 00 00 00 00 00 00 00 00 9D 14 14 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 08 E6 00 32 64 00 00 00 D0 00 A9 01 40 00 3C 00 00 00 00 00 02 00 02 00 0E 00 2E 03 D0 0D 37 00 00 00 00 00 00 00 00 0C 00 00 14 00 12 02 B2 01 66 00 00 00 00 00 00 00 00 00 00 04 04 04 04 00 04 00 00 00 00 00 50 00 50 00 00 00 00 00 00 00 00 00 00 00 00 9D 14 15 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 08 E6 00 32 64 00 00 00 D1 00 A9 01 40 00 3C 00 00 00 00 00 02 00 02 00 0E 00 2E 03 D0 0D 37 00 00 00 00 00 00 00 00 0C 00 00 14 00 12 02 B2 01 66 00 00 00 00 00 00 00 00 00 00 04 04 04 04 00 04 00 00 00 00 00 50 00 50 00 00 00 00 00 00 00 00 00 00 00 00 9D 14 14 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 08 E6 00 32 64 00 00 00 D1 00 A9 01 40 00 3C 00 00 00 00 00 02 00 02 00 0E 00 2E 03 D0 0D 37 00 00 00 00 00 00 00 00 0C 00 00 14 00 12 02 B2 01 66 00 00 00 00 00 00 00 00 00 00 04 04 04 04 00 04 00 00 00 00 00 50 00 50 00 00 00 00 00 00 00 00 00 00 00 00 9D 14 15 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 08 E6 00 32 64 00 00 00 D2 00 A9 01 40 00 3C 00 00 00 00 00 02 00 02 00 0E 00 2E 03 D0 0D 37 00 00 00 00 00 00 00 00 0C 00 00 14 00 12 02 B2 01 66 00 00 00 00 00 00 00 00 00 00 04 04 04 04 00 04 00 00 00 00 00 50 00 50 00 00 00 00 00 00 00 00 00 00 00 00 9D 14 14 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 08 E6 00 32 64 00 00 00 D2 00 A9 01 40 00 3C 00 00 00 00 00 02 00 02 00 0E 00 2E 03 D0 0D 37 00 00 00 00 00 00 00 00 0C 00 00 14 00 12 02 B2 01 66 00 00 00 00 00 00 00 00 00 00 04 04 04 04 00 04 00 00 00 00 00 50 00 50 00 00 00 00 00 00 00 00 00 00 00 00 9D 14 15 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 08 E6 00 32 64 00 00 00 D3 00 A9 01 40 00 3C 00 00 00 00 00 02 00 02 00 0E 00 2E 03 D0 0D 37 00 00 00 00 00 00 00 00 0C 00 00 14 00 12 02 B2 01 66 00 00 00 00 00 00 00 00 00 00 04 04 04 04 00 04 00 00 00 00 00 50 00 50 00 00 00 00 00 00 00 00 00 00 00 00 9D 14 14 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 08 E6 00 32 64 00 00 00 D3 00 A9 01 40 00 3C 00 00 00 00 00 02 00 02 00 0E 00 2E 03 D0 0D 37 00 00 00 00 00 00 00 00 0C 00 00 14 00 12 02 B2 01 66 00 00 00 00 00 00 00 00 00 00 04 04 04 04 00 04 00 00 00 00 00 50 00 50 00 00 00 00 00 00 00 00 00 00 00 00 9D 14 15 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 08 E6 00 32 64 00 00 00 D4 00 A9 01 40 00 3C 00 00 00 00 00 02 00 02 00 0E 00 2E 03 D0 0D 37 00 00 00 00 00 00 00 00 0C 00 00 14 00 12 02 B2 01 66 00 00 00 00 00 00 00 00 00 00 04 04 04 04 00 04 00 00 00 00 00 50 00 50 00 00 00 00 00 00 00 00 00 00 00 00 9D 14 15 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 | 08 E6 00 32 | EB 10 08 E6 00 32 64 00 00 00 EB 00 21 01 60 00 3C 00 00 FF 13 00 02 00 02 00 0F 00 32 05 36 11 E4 00 00 00 00 00 00 00 00 0C 00 00 16 00 1E 02 CD 01 74 00 00 00 00 00 00 00 00 00 00 04 04 04 04 04 04 00 04 00 00 00 58 00 58 00 00 00 00 00 00 00 02 00 00 00 00 19 16 17 0F 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 06 B4 (x0 = EB x1 = 10, ect) x11 = Aircon in automatic cleaning mode x12 = Aircon Mode Heater = 0 Cooler +1 (Off State) Cooler Manual +5 Cooler Auto +7 External Fan +9 Values +0x20 or +0xA0 observed, unknown signal. x20 = Seems to be 1 when automatic cleaning mode (1 sample) x40 = Heater Mode heater code 0 = other modes. +1 Heater Mode +3 Recycle Mode x42 = Heater Fan Speed x90 = Zone 2 Temp Target
x14: right nibble fan speed left nibble, 0 when heater used. 60 when ext fan or cooler mode. changed from 40 to 60 when on cooler auto mode. -didnt increment when set back to fan. x44 = Temp target for cooler and heater. x72,x74 = Changes with temp changes while on cooler. //Temp sensors - need to confirm, possible time delay, need to test under fan vent. x46 = Thermistor Temp x89 = Zone 2 Temp Sensor, updated from 97 03 02 17 0F BF AD while off, when fan mode enabled matches z1. x87 = Zone 1 temp sensor - only updating when system is online x88 = Unsure, seemed to match temp sensor until heater enabled changed to 0x10. possible thermistor temp? x80 = Zone State (Enabled/Disabled), LSB = Zone 1, 2nd LSB = Zone 2 x82 = Zone 2 Enabled/Disabled (Need to double check, may just be same as x80 but value for Zone 2) (Ranges observed 0-3)
F4 | 3 | Control Panel 1 |  | 00 05 00 01 |  | Only observed during system installation
FA | 3 | Control Panel 1 |  | 1 C1 0 7 |  | Observed after startup of CP1
FE | 10 | Control Panel 1 |  | Variable – During Idle is incrementing value. 3 1F 0 6 C 0 C8 0 0 1 0 FF FF FF FF FF FF 3 1F 0 6 C 0 C8 0 0 1 1 FF FF FF FF FF FF 3 1F 0 6 C 0 C8 0 0 1 2 FF FF FF FF FF FF 3 1F 0 6 C 0 C8 0 0 0 F3 FF FF FF FF FF FF 3 1F 0 6 C 0 C8 0 0 0 F4 FF FF FF FF FF FF